Heat-Pump Backup Heating: Methodology

Residential CO2 Footprint Calculator — supplementary methods for space heating by heat pumps with a backup heat source

# 1. Motivation

The calculator previously estimated emissions for households heating with an electric heat pump using a single published seasonal coefficient of performance (COP) of 1.90 in Canada and 2.00 in the United States, applied uniformly within each country. Those figures are whole-fleet seasonal averages that implicitly assume electric-resistance backup on the coldest days. They do not represent a household whose heat pump is paired with a fossil-fuel backup — a natural-gas or oil/propane furnace that carries the load once the outdoor temperature falls below a switchover point. For such a dual-fuel system the coldest, most energy-intensive part of the heating season is served by combustion rather than by the grid, which can change the estimated space-heating emissions substantially and in a direction that depends on how clean the local electricity grid is.

This document describes the revised treatment: a new survey question capturing the backup heat source, a physically-grounded heat-pump performance curve taken from field measurements, a jurisdiction-specific seasonal COP, and a per-jurisdiction economic switchover between the heat pump and the fossil backup.

# 2. New survey input: backup heat source

Respondents who report an electric heat pump as their main space-heating system are asked a follow-up question: “What is the backup heat source for your heat pump?” with response options Electric (resistance), Natural gas, Oil or propane, None, and Don’t know. In the calculator workbook this is cell B15 on the Calculator sheet. It is used only when the space-heating system is an electric heat pump; for all other systems it is ignored.

The three non-fossil answers (Electric, None, Don’t know) are treated identically: the whole heating load is met by the heat pump at its jurisdiction-specific seasonal COP, which already embeds resistance top-up on the coldest days. The two fossil answers (Natural gas, Oil or propane) trigger the dual-fuel calculation in Sections 6–7.

# 3. Heat-pump performance curve (field data)

The temperature dependence of heat-pump efficiency is taken from Gibb, Rosenow, Lowes & Hewitt (2023), “Coming in from the cold: Heat pump efficiency at low temperatures,” Joule 7, 1939–1942. That study compiles raw performance data from seven field studies spanning roughly 550 heat-pump systems and 2,760 measurements across five countries (including Canadian and US installations), and plots average measured COP against average outdoor temperature with a locally-weighted (LOWESS) trend line.

Two features make this source preferable to manufacturer-datasheet curves (e.g. Staffell et al. 2012; Ruhnau et al. 2019) for a whole-population calculator. First, it is real-world field performance rather than laboratory ratings. Second, the trend line is drawn from the study’s “mild cold climate” dataset, which is a mix of standard air-to-water and air-to-air units — not specially-engineered cold-climate heat pumps. Gibb treats cold-climate (ccASHP) equipment separately in an “extreme cold” section that we do not use, so the curve is representative of ordinary installed stock, consistent with the calculator’s standard-stock assumption.

We digitized the published trend line and fit a quadratic (RMSE 0.026 COP units):

COP_field(T) = 2.827 + 0.0807·T + 0.00151·T²      (T in °C)

Digitized values from the field curve:

| Outdoor T (°C) | -20 | -15 | -10 | -5 | 0 | +5 | +10 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| COP | 1.77 | 1.97 | 2.16 | 2.42 | 2.83 | 3.28 | 3.76 |

As a validation, this curve averages 2.68 over the −10°C to +5°C band; Gibb report a measured mean of 2.74 and median 2.62 for the same band — agreement within about two percent.

# 4. Standard-stock lockout

A standard (non cold-climate) heat pump has a low-ambient compressor cutout, below which it cannot operate and heating reverts to the backup. We impose a lockout at −15°C: below this temperature the effective COP is set to 1.0 (electric-resistance equivalent) for the electric-backup seasonal average, and for fossil-backup systems the furnace necessarily carries all load below lockout. This prevents the model from relying on the sparse, optimistic tail of the field curve below −15°C, which is drawn disproportionately from variable-capacity and cold-climate-capable units.

# 5. Seasonal integration and calibration

For each jurisdiction the daily mean temperature is modelled as a seasonal sinusoid, T(d) = T_ann − A·cos(2π(d+10)/365) with amplitude A = T_ann − T_Jan, using representative-city climate normals (annual mean and January mean). Day-to-day variability around the seasonal mean is added as a Normal distribution with standard deviation 4°C. The heating load in each temperature bin is weighted by heating demand, proportional to max(0, 18°C − T) (an 18°C base temperature).

The field curve fixes the shape of the COP–temperature relationship; its level is anchored to the published national fleet figures. A single multiplicative factor φ is applied to the curve and solved so that the load-weighted seasonal COP, integrated over a representative national climate, reproduces 1.90 in Canada and 2.00 in the United States. This yields φ_CA = 0.731 and φ_US = 0.626.

Because the climate is now handled explicitly (each jurisdiction is integrated over its own temperatures), the ratio φ_US / φ_CA = 0.855 isolates the difference in fleet performance holding climate constant: the US installed fleet performs about 15% below the Canadian fleet at equal climate. This is consistent with the Canadian stock being newer on average (recent heat-pump subsidy programs) and removes the need for an arbitrary vintage-versus-climate split — the split falls out of the data.

# 6. Jurisdiction-specific seasonal COP (electric / no fossil backup)

This section and Section 7 are two branches of one model, not two different methods. Both integrate the same field COP curve (Section 3) over the same jurisdiction climate (Section 5); they differ only in the temperature at which the heat pump stops carrying the load, and in what picks it up. With no fossil backup the heat pump runs down to its −15°C lockout and electric resistance covers the rest; because every kilowatt-hour — heat pump and resistance alike — is drawn from the grid at one emission factor, the whole season collapses to a single effective number (the jurisdiction seasonal COP below), and emissions are simply demand ÷ COP × grid factor. This collapse is exact, not an approximation: the seasonal COP is the load-weighted (harmonic) mean of the performance curve — total heat delivered divided by total electricity used — so demand ÷ COP × grid factor reproduces a bin-by-bin integration of the full curve to the last digit, discarding no temperature detail. It works only because the single grid emission factor pulls out of the sum. With a fossil backup the heat pump instead hands off at the economic switchover (Section 7) to a fuel with its own emission factor, so the calculation cannot collapse to a single COP and keeps the two-term form of Section 8. The electric case is the limiting case of that same two-term formula in which the “backup” is the grid itself.

This section concerns only heat pumps without a fossil backup (electric-resistance, none, or don’t-know). This is the case the published national figures themselves describe: 1.90 (CA) and 2.00 (US) are whole-fleet seasonal COPs that already assume electric-resistance top-up on the coldest days, which is what drags them down. For this subgroup the calculator uses the jurisdiction-specific seasonal COP obtained by integrating φ·COP_field(T) over each jurisdiction’s own climate (with resistance below the −15°C lockout), rather than a flat national value. These range from about 2.5 in the mildest jurisdictions (Vancouver, coastal/southern US) down to roughly 1.2–1.5 in the coldest (Nunavut, Northwest Territories, the northern Plains).

The φ calibration anchors this electric-backup curve to 1.90 / 2.00 at a representative national climate, so the published headline figures are recovered where heat pumps are actually concentrated — the milder, more populous provinces and states. (The simple unweighted average across all 66 jurisdictions is about 1.80 in Canada and 2.00 in the US, because it counts sparsely-populated cold territories equally with the populous south; it is not forced to equal the national figure.)

Heat pumps with a natural-gas or oil/propane backup are not set to 1.90 / 2.00. Because the furnace carries the coldest, lowest-COP hours, the heat pump operates only in its more efficient range, so its operating COP is higher — averaging roughly 2.2 for gas backup (Section 7, Section 10) — and the emissions calculation (Section 8) uses that higher operating COP for the heat-pump share, not the whole-fleet seasonal figure. The “Don’t know” main-heating mix inherits the jurisdiction-specific electric-backup COP for its heat-pump component, a small consistency improvement.

# 7. Economic switchover for fossil backup

For a dual-fuel system the outdoor temperature at which heating switches from the heat pump to the fossil furnace is modelled as the cost-minimizing (economic) switchover: a household runs whichever source delivers heat more cheaply at the margin. The heat pump is cheaper while its COP exceeds a break-even value determined by local energy prices:

COP* = (electricity price [$/kWh] × furnace efficiency) ÷ (fuel price [$/GJ] × 0.0036)

The switchover temperature is the outdoor temperature at which φ·COP_field(T) falls to COP*. Two bounds are applied. The switchover is capped at a maximum of 0°C — installed dual-fuel systems are configured heat-pump-priority above freezing, and a homeowner who paid to install a heat pump runs it in mild weather regardless of a marginal price advantage for gas. It is floored at the −15°C lockout. Between these bounds the actual economic value is used, so jurisdictions with cheap electricity (e.g. Québec, Manitoba, British Columbia hydro) run the heat pump colder, toward lockout, while jurisdictions with cheap gas keep the heat pump running only down to freezing.

Why the cap matters. Without it, the literal cost-minimizing switchover exceeds the entire heating season across most of cheap-gas North America: in Ontario, for example, delivered gas near $11/GJ against ~14¢/kWh electricity gives a break-even COP of about 3.2, which the heat pump reaches only above roughly +15°C — implying an installed heat pump sits idle all winter while gas does the heating. That is economically consistent but does not reflect how heat-pump-priority controls are actually configured, so the 0°C cap is imposed. The cap binds in most gas-served jurisdictions; the economic value governs where electricity is cheap or the backup fuel is expensive.

Oil and propane are much more expensive per GJ than natural gas, so for oil/propane backup the break-even COP is near 1 and the heat pump runs essentially to lockout almost everywhere; the fossil furnace engages only in the coldest jurisdictions with expensive electricity.

# 8. Emissions calculation

Let D be the annual useful space-heating demand (GJ), g the delivered-electricity lifecycle emission factor (kg CO2e/GJ), f_hp the fraction of D carried by the heat pump (load above switchover), COP_op the load-weighted operating COP of the heat pump above switchover, η_b the backup furnace efficiency, and e_b the backup-fuel lifecycle emission factor. Space-heating emissions for a fossil-backup heat pump are:

E = f_hp · (D / COP_op) · g  +  (1 − f_hp) · (D / η_b) · e_b

The first term is the grid electricity used by the heat pump above switchover; the second is the fossil fuel burned by the backup below switchover. For non-fossil backup the second term is zero and COP_op is the jurisdiction seasonal COP, recovering the Section 6 result. In the workbook this is computed in an auditable block (Calculator cells K24:L32) that exposes f_hp, COP_op, backup efficiency, backup emission factor, heat-pump electricity (GJ), backup fuel (GJ), and the resulting emissions, so every dual-fuel result can be traced. Emission factors are on the same lifecycle basis as the rest of the calculator: natural gas 63.3 kg CO2e/GJ and oil/propane 79.8 kg CO2e/GJ (combustion plus upstream), and the jurisdiction grid factor for electricity.

# 9. Energy prices and sources

Electricity and fuel prices enter only through their ratio in the break-even COP; absolute levels do not otherwise affect emissions. US residential electricity and natural-gas prices are state-level values compiled from EIA data (electricity in ¢/kWh; natural gas converted from $/thousand cubic feet at 1.0835 GJ per Mcf). Canadian residential electricity is by province/territory; Canadian delivered natural gas is a per-province estimate (order $9–$16/GJ, higher where gas is scarce). Heating oil and propane are treated as regional commodities (about $28/GJ in the US, $40/GJ in Canada). Furnace efficiencies used in the break-even are 0.90 for gas and 0.83 for oil/propane; the emissions calculation uses the workbook’s own jurisdiction furnace efficiencies. All prices are 2024–2026 vintage. Note that the removal of the Canadian federal consumer carbon charge in 2025 lowered delivered gas by roughly $1–$2/GJ, which pushes gas-region switchovers warmer (against the 0°C cap); the results are mildly sensitive to this.

# 10. Per-jurisdiction parameters

The table lists, for every jurisdiction, the electric-backup seasonal COP (SPF); and for each fossil backup the heat-pump load fraction f_hp, operating COP, and switchover temperature. Prices shown are the electricity (¢/kWh) and delivered gas ($/GJ) used in the switchover. Canadian and US values are in their own currencies (the switchover depends only on within-jurisdiction ratios).

Puerto Rico and the US Virgin Islands are included (66 jurisdictions total). Both are tropical, so space-heating demand is essentially zero and the heat-pump-backup logic is largely inactive there — a heat pump is effectively a cooling appliance. Their footprints are dominated instead by air-conditioning and other electricity on carbon-intensive island grids: Puerto Rico’s grid emission factor is from eGRID2022 (subregion PRMS, ≈726 g CO2e/kWh, roughly double the US average), and the US Virgin Islands (WAPA, almost entirely oil-fired) is estimated higher still. Their non-electricity parameters (heating, cooling, hot-water and housing intensities) are set from a Hawaii analogue with tropical adjustments, since jurisdiction-specific stock data are unavailable.

| Ctry | Juris (city) | SPF | gas f_hp | gas COP | gas T_sw | oil f_hp | oil COP | oil T_sw | ¢/kWh | gas $/GJ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CA | BC (Vancouver) | 2.45 | 0.89 | 2.53 | 0 | 1.00 | 2.45 | -15 | 11.4 | 13.0 |
| CA | NL (St. John's) | 2.09 | 1.00 | 2.09 | -15 | 1.00 | 2.09 | -15 | 14.8 | 30.0 |
| CA | NS (Halifax) | 2.08 | 0.48 | 2.45 | 0 | 1.00 | 2.08 | -15 | 18.3 | 20.0 |
| CA | ON (Toronto) | 2.07 | 0.46 | 2.44 | 0 | 1.00 | 2.07 | -15 | 14.1 | 11.0 |
| CA | AB (Calgary) | 1.96 | 0.37 | 2.47 | 0 | 0.97 | 1.99 | -13 | 25.8 | 9.0 |
| CA | PE (Charlottetown) | 1.93 | 0.94 | 1.98 | -12 | 0.99 | 1.95 | -15 | 18.4 | 30.0 |
| CA | NB (Fredericton) | 1.85 | 0.61 | 2.13 | -6 | 0.97 | 1.90 | -15 | 13.9 | 20.0 |
| CA | QC (Montreal) | 1.85 | 0.97 | 1.89 | -15 | 0.97 | 1.89 | -15 | 7.8 | 16.0 |
| CA | YT (Whitehorse) | 1.58 | 0.59 | 1.97 | -11 | 0.80 | 1.82 | -15 | 18.7 | 30.0 |
| CA | SK (Regina) | 1.55 | 0.19 | 2.48 | 0 | 0.78 | 1.80 | -15 | 19.9 | 10.0 |
| CA | MB (Winnipeg) | 1.50 | 0.18 | 2.48 | 0 | 0.73 | 1.79 | -15 | 10.2 | 9.5 |
| CA | NT (Yellowknife) | 1.25 | 0.14 | 2.50 | 0 | 0.14 | 2.50 | 0 | 41.0 | 30.0 |
| CA | NU (Iqaluit) | 1.23 | 0.13 | 2.40 | 0 | 0.14 | 2.38 | -0 | 35.4 | 30.0 |
| US | PR (San Juan) | 2.75 | 1.00 | 2.75 | -4 | 1.00 | 2.75 | 0 | 25.0 | 40.0 |
| US | VI (St. Thomas) | 2.75 | 1.00 | 2.75 | 0 | 1.00 | 2.75 | 0 | 45.0 | 40.0 |
| US | HI (Honolulu) | 2.73 | 1.00 | 2.73 | 0 | 1.00 | 2.73 | 0 | 46.6 | 56.2 |
| US | FL (Miami) | 2.67 | 1.00 | 2.67 | 0 | 1.00 | 2.67 | -13 | 15.4 | 20.3 |
| US | CA (Los Angeles) | 2.49 | 1.00 | 2.49 | 0 | 1.00 | 2.49 | 0 | 35.3 | 19.1 |
| US | AZ (Phoenix) | 2.45 | 1.00 | 2.45 | 0 | 1.00 | 2.45 | -13 | 15.5 | 18.2 |
| US | LA (New Orleans) | 2.41 | 1.00 | 2.42 | 0 | 1.00 | 2.41 | -15 | 14.4 | 12.9 |
| US | SC (Charleston) | 2.29 | 0.99 | 2.30 | 0 | 1.00 | 2.29 | -9 | 17.1 | 16.6 |
| US | MS (Jackson) | 2.25 | 0.98 | 2.27 | 0 | 1.00 | 2.25 | -9 | 16.8 | 17.1 |
| US | TX (Dallas) | 2.25 | 0.98 | 2.26 | 0 | 1.00 | 2.25 | -9 | 17.0 | 22.7 |
| US | NV (Las Vegas) | 2.25 | 0.98 | 2.26 | 0 | 1.00 | 2.25 | -15 | 14.3 | 9.3 |
| US | AL (Birmingham) | 2.21 | 0.96 | 2.23 | 0 | 1.00 | 2.21 | -8 | 17.4 | 16.5 |
| US | GA (Atlanta) | 2.21 | 0.96 | 2.23 | 0 | 1.00 | 2.21 | -13 | 15.4 | 17.0 |
| US | WA (Seattle) | 2.14 | 0.92 | 2.19 | 0 | 1.00 | 2.14 | -15 | 14.4 | 12.0 |
| US | NC (Charlotte) | 2.12 | 0.92 | 2.17 | 0 | 1.00 | 2.12 | -11 | 16.3 | 14.8 |
| US | AR (Little Rock) | 2.12 | 0.99 | 2.13 | -4 | 1.00 | 2.12 | -15 | 14.2 | 22.7 |
| US | OR (Portland OR) | 2.12 | 0.91 | 2.17 | 0 | 1.00 | 2.12 | -12 | 15.8 | 16.6 |
| US | TN (Nashville) | 2.06 | 0.86 | 2.13 | 0 | 1.00 | 2.06 | -15 | 14.9 | 14.3 |
| US | VA (Richmond) | 2.04 | 0.84 | 2.13 | 0 | 1.00 | 2.04 | -8 | 17.4 | 17.3 |
| US | OK (Oklahoma City) | 2.03 | 0.84 | 2.12 | 0 | 1.00 | 2.03 | -15 | 13.3 | 14.7 |
| US | KY (Louisville) | 2.00 | 0.79 | 2.11 | 0 | 1.00 | 2.00 | -14 | 15.0 | 17.6 |
| US | NM (Albuquerque) | 2.00 | 0.79 | 2.11 | 0 | 1.00 | 2.00 | -14 | 15.2 | 11.0 |
| US | DC (Washington DC) | 1.99 | 0.79 | 2.11 | 0 | 1.00 | 1.99 | -13 | 15.5 | 15.7 |
| US | DE (Wilmington) | 1.96 | 0.74 | 2.10 | 0 | 0.96 | 1.99 | -5 | 18.8 | 15.8 |
| US | MD (Baltimore) | 1.96 | 0.74 | 2.10 | 0 | 0.74 | 2.10 | 0 | 22.1 | 15.9 |
| US | PA (Philadelphia) | 1.96 | 0.74 | 2.10 | 0 | 0.74 | 2.10 | 0 | 21.5 | 15.4 |
| US | WV (Charleston WV) | 1.94 | 0.71 | 2.09 | 0 | 1.00 | 1.94 | -11 | 16.1 | 12.9 |
| US | NJ (Newark) | 1.91 | 0.68 | 2.09 | 0 | 0.68 | 2.09 | 0 | 23.5 | 13.1 |
| US | KS (Wichita) | 1.91 | 0.68 | 2.08 | 0 | 1.00 | 1.91 | -12 | 15.8 | 14.4 |
| US | MO (St. Louis) | 1.91 | 0.68 | 2.08 | 0 | 1.00 | 1.91 | -15 | 14.0 | 14.5 |
| US | NY (New York City) | 1.90 | 0.65 | 2.09 | 0 | 0.65 | 2.09 | 0 | 29.4 | 17.4 |
| US | CO (Denver) | 1.89 | 0.63 | 2.09 | 0 | 0.99 | 1.89 | -10 | 16.5 | 10.7 |
| US | ID (Boise) | 1.88 | 0.62 | 2.09 | 0 | 1.00 | 1.88 | -15 | 12.7 | 7.2 |
| US | MA (Boston) | 1.86 | 0.59 | 2.08 | 0 | 0.59 | 2.08 | 0 | 29.4 | 25.1 |
| US | RI (Providence) | 1.84 | 0.57 | 2.08 | 0 | 0.57 | 2.08 | 0 | 28.3 | 14.3 |
| US | UT (Salt Lake City) | 1.84 | 0.56 | 2.08 | 0 | 1.00 | 1.84 | -15 | 13.3 | 10.4 |
| US | OH (Columbus) | 1.82 | 0.53 | 2.08 | 0 | 0.77 | 1.94 | -3 | 19.5 | 12.7 |
| US | IN (Indianapolis) | 1.81 | 0.53 | 2.08 | 0 | 0.93 | 1.86 | -7 | 17.9 | 11.5 |
| US | WY (Cheyenne) | 1.80 | 0.50 | 2.10 | 0 | 1.00 | 1.80 | -15 | 14.7 | 10.0 |
| US | CT (Hartford) | 1.78 | 0.48 | 2.08 | 0 | 0.48 | 2.08 | 0 | 32.2 | 18.0 |
| US | MT (Billings) | 1.77 | 0.47 | 2.09 | 0 | 1.00 | 1.77 | -15 | 13.9 | 7.8 |
| US | IL (Chicago) | 1.75 | 0.43 | 2.08 | 0 | 0.56 | 1.99 | -2 | 20.5 | 11.2 |
| US | MI (Detroit) | 1.75 | 0.43 | 2.08 | 0 | 0.46 | 2.06 | -0 | 21.4 | 10.4 |
| US | NH (Manchester) | 1.71 | 0.39 | 2.09 | 0 | 0.39 | 2.09 | 0 | 27.2 | 19.6 |
| US | NE (Omaha) | 1.70 | 0.38 | 2.08 | 0 | 1.00 | 1.71 | -15 | 13.3 | 11.1 |
| US | WI (Milwaukee) | 1.69 | 0.37 | 2.09 | 0 | 0.61 | 1.91 | -4 | 19.2 | 8.8 |
| US | ME (Portland ME) | 1.68 | 0.36 | 2.10 | 0 | 0.36 | 2.10 | 0 | 28.4 | 14.8 |
| US | IA (Des Moines) | 1.67 | 0.35 | 2.09 | 0 | 0.99 | 1.68 | -15 | 13.9 | 11.1 |
| US | AK (Anchorage) | 1.65 | 0.35 | 2.10 | 0 | 0.35 | 2.10 | 0 | 27.4 | 12.0 |
| US | VT (Burlington) | 1.63 | 0.31 | 2.10 | 0 | 0.31 | 2.10 | 0 | 24.6 | 15.4 |
| US | MN (Minneapolis) | 1.58 | 0.28 | 2.10 | 0 | 0.83 | 1.68 | -10 | 16.4 | 13.2 |
| US | SD (Sioux Falls) | 1.58 | 0.28 | 2.10 | 0 | 0.97 | 1.61 | -15 | 14.5 | 10.4 |
| US | ND (Fargo) | 1.45 | 0.21 | 2.12 | 0 | 0.87 | 1.55 | -15 | 12.3 | 7.6 |

# 11. Limitations

The model assumes a single representative-city climate per jurisdiction; within-jurisdiction climate variation (e.g. upstate New York versus New York City) is not resolved. The economic switchover assumes a rational cost-minimizing setpoint bounded by heat-pump-priority behavior; actual installer setpoints vary and are not observed. The field COP curve is a cross-study average and does not distinguish air-to-air from air-to-water or capture individual system quality. Delivered gas prices for Canada and the oil/propane commodity prices are approximate. The lockout (−15°C), the 0°C switchover cap, and the daily temperature variability (σ = 4°C) are modelling choices; the space-heating results for cold-climate, fossil-backup respondents are most sensitive to the first two, which are documented here so they can be varied in sensitivity analysis.